## Slide 1
Condo Building
7 buildings
1 main meter 33kV 3 phase TOU
280 condos/ single phase PEA meters
Each building has 33kV/ 380V xformer
Then 380V to 6 breaker to 4 x floors of
residential units, 1 to lift, 1 to common building
(same layout in each of 7 buildings)
Billing for all 7 buildings by 33kV TOU meter
280 condos receive normal residential bill monthly
from 280 normal meter read by PEA (not TOU)
Common area bill ₿ is calculated………..
Main TOU meter ₿ less Σ all (280) residential meters ₿
Goal ….
A solar power system to significantly reduce the common
area bill (currently average 100,000 ₿ high 120K, low 80K)
Average 730 kWh/ day, 30 kW .
Sum of all condo units 4666kWh /day 194kW.
Condos 86%, common 14% of total
Main meter 5x common bill
33kV
PEA
TOU main meter
33kV
A
B
C
D
E
F
G
33kV / 380V
Step down
transformer
MDB
Residential
Meters
Lift and other common
All 7 buildings A-F same as A
Current electrical plan

## Slide 2: Entropy proposed plan
2 x 55kW systems on the 2 highest power buildings
Energy saving 45,000/ month rainy season
Energy saving 90,000/ month rainy season
Building 33kV bus
33 kV/ 380 VAC
30 kW inverter
33 kW array
3 x 33 kW on 3
different buildings
Common area bill ₿ is calculated………..
Main TOU meter ₿ less Σ all (280) residential meters ₿
Solar power at 380V will go to
Building common (reducing PEA demand at peak rate)
Condo meters (owner will pay to PEA without drawing from PEA and will cut net common PEA bill at residential rate due to bill formula above
Can 3 of 7 buildings support savings to wipe out most of common bill without a building excess from solar?
Worst case excess solar 55kW, does this exceed building meter capacity to consume.
Average condo load; 194 kW/ 7 buildings = 28kW
Average common load; 30 /7 = 4 kW
Under peak theoretical solar production each of 3 buildings can utilize/ gain value 97% of power generated
380V
33 kV
Common
circuits
Condo
unit
meters